## Datasheet
#VALUE! |  |  |  | F11280 - Generator Datasheet Template
DOCUMENT NO : |  |  |  | Asset ID: | [6 empty] | Project/Contract No:
TITLE : <<Site>> LV Generator Datasheet
EQUIPMENT DATASHEET
LV DIESEL POWER GENERATOR ( xxxkVA )
CLIENT : |  |  |  | REV: | PREPARED: |  | CHECKED: |  | APPROVED: |  | DESCRIPTION
UNITYWATER |  |  |  |  | DATE | INITIAL | DATE | INITIAL | DATE | SIGNATURE
|  |  |  | 1 | 2024-04-16 | AP/RP | 2024-04-16 | RP, TGS | 2024-06-21 | IB | TEMPLATE APPROVED FOR USE
PLANT LOCATION : XXXXX |  |  |  | 2 | 2026-06-22 | T. Stewart | 2024-06-22 | T. Stewart |  |  | Periodic review: No Changes
DESCRIPTION |  |  |  |  | UNIT OF MEASURE | DATA TO BE CONFIRMED BY VENDOR |  |  |  |  | VENDORS RESPONSE | Rev
GENERAL PACKAGE DATA |  | 1 | Supplier |  | - | VTA | [5 empty] | 0
|  | 2 | Manufacturer |  | - | VTA | [5 empty] | 0
|  | 3 | Place of Manufacturer |  | - | VTA | [5 empty] | 0
|  | 4 | Model No. |  | - | VTA | [5 empty] | 0
|  | 5 | Applicable Codes and Standards |  | - | ISO8528, IEC 8528, GB755, BS5000, ISO3046, IEC34-1, AS3000, AS60034, AS61439 Any other relevant australian standards or regulations. | [5 empty] | 0
|  | 6 | Technical Specification |  | - | Pr9913 - Specification for Acoustic Enclosed Generators at Unitywater Sites (Supply and Installation) | [5 empty] | 0
|  | 7 | Duty Type |  | - | Emergency Standby Power / S1 | [5 empty] | 0
|  | 8 | Prime Rating of DEA Package |  | kW | VTA | [5 empty] | 0
|  | 9 | Standby Rating of DEA Package |  | kVA | VTA | [5 empty] | 0
|  | 10 | Power Factor at Maximum Rating |  | - | 0.8 or better | [5 empty] | 0
|  | 11 | Design Ambient Air Temperature |  | °C | Min: -5°C, Max 45°C | [5 empty] | 0
|  | 12 | Mounting Type |  | - | Skid Mounted | [5 empty] | 0
|  | 13 | Transportable with Lifting Lugs |  | - | Yes | [5 empty] | 0
|  | 14 | Acoustic Enclosure Construction Material |  | - | VTA. Must be suitable for corrosive environment | [5 empty] | 0
|  | 15 | Acoustic Enclosure Paint Specification and Colour |  | - | VTA | [5 empty] | 0
|  | 16 | Acoustic Enclosure Ingress Protection Rating |  | - | Min IP56 | [5 empty] | 0
|  | 17 | Acoustic Enclosure Cooling Method |  | - | Natural/Forced | [5 empty] | 0
|  | 18 | Acoustic Enclosure Air Discharge Location |  | - | VTA | [5 empty] | 0
|  | 19 | Acoustic Enclosure Air Filters |  | - | VTA | [5 empty] | 0
|  | 20 | Acoustic Enclosure Access Types |  | - | Lockable Doors | [5 empty] | 0
|  | 21 | Enclosure Viewing Window for Electrical Panel |  | - | VTA | [5 empty] | 0
|  | 22 | Design Life |  | Years | Electrical Components 20 years Mechanical Components 40 years | [5 empty] | 0
|  | 23 | Design Operating Hours |  | Hrs | xxhrs per Day | [5 empty] | 0
|  | 24 | Max noise level |  | dB(A) | Shall not exceed 85 dB(A) at 1 m or 5dBA above the surrounding environment noise level measured at the boundary, whichever is lower. When installed near sensitive environments, such as residential properties, noise shall not exceed 30 dBA at the property boundary consistent with the Acoustic Quality Objectives in the Environmental Protection (Noise) Policy 2019 | [5 empty] | 0
|  | 25 | Engine/Alternator Vibration Isolators |  | - | VTA | [5 empty] | 0
|  | 26 | Package Dimensions (L X W X H) |  | mm | VTA | [5 empty] | 0
|  | 27 | Package Weight (Wet) |  | kg | VTA | [5 empty] | 0
|  | 28 | Skid Frame/Base material |  | - | VTA | [5 empty] | 0
|  | 29 | Skid Frame/Base corrossion protection |  | - | Hot Dipped Galvanised (HDG) | [5 empty] | 0
|  | 30 | Load Bank on skid |  | - | UW to advise if required | [5 empty] | 0
|  | 31 | Internal Load Bank |  | - | Vendor to advise if required | [5 empty] | 0
|  | 32 | External Load Bank Connection |  | - | If Required | [5 empty] | 0
|  | 33 | Onboard Auto Transfer Switch |  | - | Not Required | [5 empty] | 0
ALTERNATOR DATA |  | 34 | Manufacturer |  | - | VTA | [5 empty] | 0
|  | 35 | Type & Model No. |  | - | VTA | [5 empty] | 0
|  | 36 | Paint specification and colour |  | - | VTA | [5 empty] | 0
|  | 37 | Applicable Codes and Standards |  | - | VTA | [5 empty] | 0
|  | 38 | Rated Voltage |  | V (ac) | 400 | [5 empty] | 0
|  | 39 | Rated Frequency |  | Hz | 50 | [5 empty] | 0
|  | 40 | Max continuous rating |  | kVA | xxxKVA after all de-rating including enclosure internal temp | [5 empty] | 0
|  | 41 | Power Factor (Lag/Lead) |  | pf | 0.8 | [5 empty] | 0
|  | 42 | Stator Connection |  | - | Star | [5 empty] | 0
|  | 43 | Neutral Earthing Method |  | - | Solid, Note: MEN at Gen to be disconnected. MEN at site main switchobard only | [5 empty] | 0
|  | 44 | Phase rotation |  | - | as per site - VTA correct rotation prior to termination | [5 empty] | 0
|  | 45 | System max. fault current (3-phase sym) 1 Second |  | kA | VTA | [5 empty] | 0
ALTERNATOR DATA (continued) |  | 46 | Protection CTs |  | - | VTA | [5 empty] | 0
|  | 47 | Rotation facing coupling end |  | - | Clockwise | [5 empty] | 0
|  | 48 | Insulation Class (minimum) |  | - | Class F | [5 empty] | 0
|  | 49 | Temperature rise |  | °C | VTA | [5 empty] | 0
|  | 50 | Speed |  | rpm | VTA | [5 empty] | 0
|  | 51 | X/R Ratio |  | - | VTA | [5 empty] | 0
|  | 52 | Alternator Efficiency at Full Load |  | % | 93% or higher | [5 empty] | 0
|  | 53 | Alternator Efficiency at 75% Load |  | % | VTA | [5 empty] | 0
|  | 54 | Alternator Efficiency at 50% Load |  | % | VTA | [5 empty] | 0
|  | 55 | Type of excitation |  | - | Self | [5 empty] | 0
|  | 56 | Suitable for parallel operation with the system |  | - | UW to advise if required | [5 empty] | 0
|  | 57 | Winding temperature detectors (No. & type) |  | - | VTA | [5 empty] | 0
|  | 58 | Alternator Anti-condensation Heaters |  | kW | VTA | [5 empty] | 0
|  | 59 | Number Alternator Anti-condensation Heaters |  | - | VTA | [5 empty] | 0
|  | 60 | Bearing type (DE & NDE) |  | - | VTA | [5 empty] | 0
|  | 61 | Lubrication |  | - | VTA | [5 empty] | 0
|  | 62 | Terminal Box type, size and arrangement |  | - | VTA | [5 empty] | 0
|  | 63 | Synchronous (Xd) |  | % | VTA | [5 empty] | 0
|  | 64 | Transient (X'd) |  | % | VTA | [5 empty] | 0
|  | 65 | Subtransient (X''d) |  | % | VTA | [5 empty] | 0
|  | 66 | Negative Sequence (X2) |  | % | VTA | [5 empty] | 0
|  | 67 | Zero Sequence (X0) |  | % | VTA | [5 empty] | 0
|  | 68 | Positive Sequence (R1) |  | % | VTA | [5 empty] | 0
|  | 69 | Negative Sequence (R2) |  | % | VTA | [5 empty] | 0
|  | 70 | Zero Sequence (R0) |  | % | VTA | [5 empty] | 0
|  | 71 | Generator Synch with Normal Supply |  | - | Not Required | [5 empty] | 0
EXCITATION SYSTEM |  | 72 | Manufacturer & Model |  | - | VTA | [5 empty] | 0
|  | 73 | Permanent Magnet Pilot Generator (PMG) Type |  | - | VTA | [5 empty] | 0
|  | 74 | Diode bridge element failure detection |  | - | VTA | [5 empty] | 0
|  | 75 | Hermetically sealed |  | - | VTA | [5 empty] | 0
AUTOMATIC VOLTAGE REGULATOR SYSTEM (AVR) |  | 76 | Manufacturer & Model |  | - | VTA | [5 empty] | 0
|  | 77 | Type |  | - | VTA | [5 empty] | 0
|  | 78 | IEC 60034-16-12 model type |  | - | VTA | [5 empty] | 0
|  | 79 | Solid state regulator |  | - | VTA | [5 empty] | 0
|  | 80 | Max excitation limits |  | V | VTA | [5 empty] | 0
|  | 81 | Max volts/hertz limits |  | V/Hz | VTA | [5 empty] | 0
AUTOMATIC VOLTAGE REGULATOR SYSTEM (AVR) (continued) |  | 82 | Output voltage set point adjustment |  | % | VTA | [5 empty] | 0
|  | 83 | Voltage regulation under 100% load rejection |  | % | VTA | [5 empty] | 0
|  | 84 | Voltage regulation under 50% load acceptance, initial load 0% |  | % | VTA | [5 empty] | 0
|  | 85 | Voltage regulation under 50% load acceptance, initial load 50% |  | % | VTA | [5 empty] | 0
|  | 86 | Under frequency protection |  | - | VTA | [5 empty] | 0
|  | 87 | Over voltage protection |  | - | VTA | [5 empty] | 0
|  | 88 | Voltage regulation under transient conditions |  | % | VTA | [5 empty] | 0
|  | 89 | Functional without external power supply |  | - | VTA | [5 empty] | 0
GOVERNOR |  | 90 | Type |  | - | Electronic | [5 empty] | 0
|  | 91 | Manual Operating Speed Adjustment Available |  | - | Required including locking of adjustment after setting | [5 empty] | 0
ELECTRICAL ONBOARD CIRCUIT BREAKER PANEL |  | 92 | Panel Construction Material |  | - | VTA | [5 empty] | 0
|  | 93 | Panel Paint Specification and Colour |  | - | VTA | [5 empty] | 0
|  | 94 | Panel IP Rating |  | - | VTA | [5 empty] | 0
|  | 95 | 4 Pole Main CB |  | - | VTA - To be suitable as per AS3010 requirements | [5 empty] | 0
|  | 96 | Main CB Make & Model |  |  | VTA | [5 empty] | 0
|  | 97 | Main CB Type |  | - | VTA - ACB/MCCB | [5 empty] | 0
ELECTRICAL CONTROL PANEL |  | 98 | Panel Construction Material |  | - | VTA | [5 empty] | 0
|  | 99 | Panel Paint Specification and Colour |  | - | VTA | [5 empty] | 0
|  | 100 | Panel IP Rating |  | - | VTA | [5 empty] | 0
|  | 101 | AC and DC CB's - control/small power |  | - | MCB (AC Auxilliary power MCB's to be in separate IP44 Load Centre style enclosure within Genset Enclosure) | [5 empty] | 0
|  | 102 | DC CB's - control |  | - | Double Pole | [5 empty] | 0
|  | 103 | DC Power Supply |  | V | 240VAC/24VDC, 30mA RCD | [5 empty] | 0
|  | 104 | DC Power Supply Rating |  | VA | VTA | [5 empty] | 0
|  | 105 | Ventillation |  | - | Forced/Natural | [5 empty] | 0
|  | 106 | Fan Voltage |  | V | VTA | [5 empty] | 0
|  | 107 | Thermostat fan control |  | - | VTA | [5 empty] | 0
CABLE CONNECTIONS |  | 108 | Main 415V Cable Connection |  | mm² | VTA(max) | [5 empty] | 0
|  | 109 | Auxiliary 240V Cable Connection |  | mm² | VTA(max) | [5 empty] | 0
|  | 110 | Control Cabling |  | mm² | minimum 1.5mm² | [5 empty] | 0
|  | 111 | Active Conductors |  | No/phase | VTA | [5 empty] | 0
|  | 112 | Neutral Conductors |  | No/phase | VTA | [5 empty] | 0
|  | 113 | Output terminal rating |  | Amps | VTA | [5 empty] | 0
|  | 114 | Earth Bar |  |  | tinned copper | [5 empty] | 0
|  | 115 | Earth Bar size |  | mm | VTA | [5 empty] | 0
CONTROL AND INDICATION |  | 116 | Controller Type Offered - Make and Model |  | - | VTA | [5 empty] | 0
CONTROL AND INDICATION (MECHANICAL SERVICE INDICATOR) |  | 117 | Lube oil filter |  | - | VTA | [5 empty] | 0
|  | 118 | Air filter |  | - | VTA | [5 empty] | 0
CONTROL AND INDICATION (INDICATOR LAMPS) |  | 119 | Running |  | - | VTA | [5 empty] | 0
|  | 120 | General Fault |  | - | VTA | [5 empty] | 0
CONTROL AND INDICATION (DISPLAY TYPE) |  | 121 | Coolant temperature |  | °C | VTA | [5 empty] | 0
|  | 122 | Coolant water pressure |  | kPag | VTA | [5 empty] | 0
|  | 123 | Lubricating oil temperature |  | °C | VTA | [5 empty] | 0
|  | 124 | Lubricating oil pressure |  | kPag | VTA | [5 empty] | 0
|  | 125 | Lubricating oil filter differential pressure |  | kPa | VTA | [5 empty] | 0
|  | 126 | Air filter differential pressure |  | kPa | VTA | [5 empty] | 0
|  | 127 | Engine speed |  | RPM | VTA | [5 empty] | 0
|  | 128 | Battery Voltage |  | V | VTA | [5 empty] | 0
|  | 129 | Phase Currents (x3) |  | Amps | VTA | [5 empty] | 0
|  | 130 | Phase Voltages (x3) |  | V | VTA | [5 empty] | 0
|  | 131 | Frequency |  | Hz | VTA | [5 empty] | 0
|  | 132 | Day Tank Fuel Level |  | % | VTA | [5 empty] | 0
|  | 133 | Hours Run Counter |  | Hrs | VTA | [5 empty] | 0
|  | 134 | Power Factor of Load |  | - | VTA | [5 empty] | 0
CONTROL AND INDICATION (WARNING ALARMS) |  | 135 | High coolant water temperature |  | - | VTA | [5 empty] | 0
|  | 136 | Coolant level low |  | - | VTA | [5 empty] | 0
|  | 137 | Low oil pressure |  | - | VTA | [5 empty] | 0
|  | 138 | Lube oil sump level low |  | - | VTA | [5 empty] | 0
|  | 139 | Day tank fuel level low |  | - | VTA | [5 empty] | 0
|  | 140 | Battery charger fault |  | - | VTA | [5 empty] | 0
|  | 141 | Water in fuel filter |  | - | VTA | [5 empty] | 0
|  | 142 | Winding Temperature High |  | - | VTA | [5 empty] | 0
|  | 143 | Fuel Bund liquid present |  | - | VTA | [5 empty] | 0
|  | 144 | Vibration high |  | - | VTA | [5 empty] | 0
|  | 145 | Control Panel high temperature |  | - | VTA | [5 empty] | 0
CONTROL AND INDICATION (SHUTDOWN ALARMS) |  | 146 | Phase Failure |  | - | VTA | [5 empty] | 0
|  | 147 | Voltage - over/under |  | - | VTA | [5 empty] | 0
|  | 148 | Frequency - over/under |  | - | VTA | [5 empty] | 0
|  | 149 | High coolant water temperature |  | - | VTA | [5 empty] | 0
|  | 150 | Coolant level low |  | - | VTA | [5 empty] | 0
|  | 151 | Day Tank Fuel level high |  | - | VTA | [5 empty] | 0
|  | 152 | Day Tank Fuel level Very low (Empty) |  |  | VTA | [5 empty] | 0
|  | 153 | Winding over temperature |  | - | VTA | [5 empty] | 0
|  | 154 | Alternator Undervoltage |  | - | VTA | [5 empty] | 0
|  | 155 | Alternator Overvoltage |  | - | VTA | [5 empty] | 0
|  | 156 | Circuit Breaker Protection Trip |  | - | VTA | [5 empty] | 0
|  | 157 | Engine Fail to Start after 3 Cranks |  | - | VTA | [5 empty] | 0
|  | 158 | Vibration High |  | - | VTA | [5 empty] | 0
|  | 159 | E-stop activated |  | - | VTA | [5 empty] | 0
|  | 160 | Shut Inlet valve when Fuel tank level high |  | - | VTA | [5 empty] | 0
CONTROL AND INDICATION (CONTROL) |  | 161 | Auto - start/stop |  | - | VTA | [5 empty] | 0
|  | 162 | Manual Local - start/stop |  | - | VTA | [5 empty] | 0
|  | 163 | Emergency Stop - Category to AS4024 |  | - | VTA | [5 empty] | 0
CONTROL AND INDICATION (REMOTE MONITORING) |  | 164 | Generator General Warning |  | - | VTA | [5 empty] | 0
|  | 165 | Generator General Fault |  | - | VTA | [5 empty] | 0
|  | 166 | Generator Ready to Start |  | - | VTA | [5 empty] | 0
|  | 167 | Generator Running |  | - | VTA | [5 empty] | 0
|  | 168 | Generator Failed to Start |  | - | VTA | [5 empty] | 0
|  | 169 | Day Tank Low Fuel Level |  | - | VTA | [5 empty] | 0
|  | 170 | Generator Main CB closed |  | - | VTA | [5 empty] | 0
|  | 171 | Battery Warning |  | - | VTA | [5 empty] | 0
|  | 172 | Battery Charger Fault |  | - | VTA | [5 empty] | 0
|  | 173 | Generator Enclosure Access Door open |  | - | VTA | [5 empty] | 0
|  | 174 | Generator Emergency Stop Activated |  | - | VTA | [5 empty] | 0
ENGINE DATA |  | 175 | Manufacturer |  | - | VTA | [5 empty] | 0
|  | 176 | Model No. |  | - | VTA | [5 empty] | 0
|  | 177 | Type |  | - | Diesel | [5 empty] | 0
|  | 178 | Duty |  | - | Refer Item 7 | [5 empty] | 0
|  | 179 | Power at Engine Shaft (Continuous Duty) |  | kW | VTA | [5 empty] | 0
|  | 180 | Power at Engine Shaft (Intermittent Duty) |  | kW | VTA | [5 empty] | 0
|  | 181 | Power Loss to Auxiliaries |  | kW | VTA | [5 empty] | 0
|  | 182 | Ambient Air Temperature for Rating |  | °C | Refer Item 11 | [5 empty] | 0
|  | 183 | Engine Speed |  | RPM | VTA | [5 empty] | 0
|  | 184 | Intercooler Type |  | - | Air to Air or Air to Water | [5 empty] | 0
|  | 185 | Fuel Consumption at Rated Load |  | L/Hr | VTA | [5 empty] | 0
|  | 186 | Fuel Consumption Curves Provided With Tender |  | - | Consumption data at nominal duty points required | [5 empty] | 0
|  | 187 | Drive Type |  | - | Direct | [5 empty] | 0
COOLING SYSTEM |  | 188 | Type |  | - | Radiator | [5 empty] | 0
|  | 189 | Fan Driver |  | - | Engine Shaft | [5 empty] | 0
|  | 190 | Jacket Water Heater |  | - | VTA | [5 empty] | 0
|  | 191 | Cooling System Materials and Construction |  | - | VTA | [5 empty] | 0
LUBRICATION SYSTEM |  | 192 | Prelube Pump |  | - | VTA | [5 empty] | 0
|  | 193 | Engine Driven Lubrication Pump |  | - | Required | [5 empty] | 0
|  | 194 | Lube Oil Filter |  | - | The engine lubricating oil system shall incorporate a full-flow engine-mounted filter of the replaceable element type fitted with an automatic by-pass valve. A switch shall provide indication to the control system of bypass operation | [5 empty] | 0
|  | 195 | Oil Make Up Tank |  | - | Not Required | [5 empty] | 0
|  | 196 | Lube Oil Cooler |  | - | The engine shall be fitted with a direct engine-mounted full-flow oil cooler with an automatic by-pass valve. A switch shall provide indication to the control system of by-pass operation | [5 empty] | 0
|  | 197 | Manually Operated Oil Fill/Empty Pump |  | - | VTA | [5 empty] | 0
FUEL SYSTEM |  | 198 | Type |  | - | Diesel in accordance with AS 3570 | [5 empty] | 0
|  | 199 | Engine Driven Fuel Injection Pump |  | - | Required | [5 empty] | 0
|  | 200 | Water and Sediment Trap / Prefilter |  | - | VTA | [5 empty] | 0
|  | 201 | Main Fuel Heater |  | - | VTA | [5 empty] | 0
|  | 202 | Manual Fuel Priming Pump |  | - | VTA | [5 empty] | 0
|  | 203 | Day Tank |  | - | Double Bunded | [5 empty] | 0
|  | 204 | Day Tank Bund Volume Capacity |  | L | VTA @ 120% of Rated Load | [5 empty] | 0
|  | 205 | Day Tank Construction Material |  | - | VTA | [5 empty] | 0
|  | 206 | Day Tank Fuel Capacity |  | L | VTA | [5 empty] | 0
|  | 207 | Day Tank Dimension |  | mm | LxWxH | [5 empty] | 0
|  | 208 | Engine Run Time at 75% of Full Load - Day Tank |  | hrs | VTA | [5 empty] | 0
|  | 209 | Automatic Fuel Replenishment System |  | - | As required by Project Specification. | [5 empty] | 0
|  | 210 | Facility Connecting External Gravity Fed Fuel Tank |  | - | As required by Project Specification. | [5 empty] | 0
|  | 211 | Fuel bunds provided with drain valve and plug |  | - | Required | [5 empty] | 0
AIR INTAKE SYSTEM |  | 212 | Engine Air Filter with Service Indicator |  | - | VTA | [5 empty] | 0
|  | 213 | Air Intake System Materials and Construction |  | - | VTA | [5 empty] | 0
EXHAUST SYSTEM |  | 214 | Manufacturer |  | - | VTA | [5 empty] | 0
|  | 215 | Type |  | - | Industrial Grade | [5 empty] | 0
|  | 216 | Insulated and Sheathed Within Enclosure |  | - | VTA | [5 empty] | 0
|  | 217 | Exhaust System Materials and Construction |  | - | VTA | [5 empty] | 0
STARTING SYSTEM |  | 218 | Charger Manufacturer |  | - | VTA | [5 empty] | 0
|  | 219 | Charger Type |  | - | VTA | [5 empty] | 0
|  | 220 | Charger Rating |  | Amps, V | VTA | [5 empty] | 0
|  | 221 | Type of Batteries |  | - | VRLA | [5 empty] | 0
|  | 222 | Battery Cell Voltage |  | V | 12/24VDC | [5 empty] | 0
|  | 223 | Battery Cells |  | No. | VTA | [5 empty] | 0
|  | 224 | Batery Recharge Time from flat |  | Hrs | VTA | [5 empty] | 0
|  | 225 | Generator Start-up time and accept load |  | sec | VTA | [5 empty] | 0
ENGINE - ALTERNATOR COUPLING |  | 226 | Manufacturer |  | - | VTA | [5 empty] | 0
|  | 227 | Type |  | - | Direct | [5 empty] | 0
|  | 228 | Construction Description |  | - | VTA | [5 empty] | 0
No. | Notes :
1 | VTA - Vendor to Advise
2 | Vendor must advise all departure from Pr9913
3 | Vendor shall deliver documentation as per Pr9913
4 | Vendor shall update this datasheet and submit with bid proposal - all items must be updated in 'VENDORS RESPONSE' column