## Instructions
| Project Name: |  | Name
| Finance No: |  | No
| Project Address: |  | Address
Instructions
Sewer Pump Station Commissioning Worksheet
1) This Worksheet shall be completed during commissioning in conjunction with project specific SPS Check Sheets
2) The completed worksheet containing parameters as commissioned shall be provided to Operations and included in the Asset Manual
LEGEND
| 0 | - values to be entered by user
| 0 | - calculated values

## Project Info
| Project Name: | Name
| Finance No: | No
| Project Address: | Address
Project Location
EXAMPLE
EXAMPLE
EXAMPLE
Insert site location (Picture/Diagram/Map).
Provide conclusive site identification ie: Google Map or similar

## Setup
| Project Name: |  |  | Name |  |  |  | Project Name: |  | Name
| Finance No: |  |  | No |  |  |  | Finance No: |  | No
| Project Address: |  |  | Address |  |  |  | Project Address: |  | Address
Well Design Setup
|  |  | Value | Unit
Hydrostatic Probe (Calibrated Length) |  |  | 10 | m
Installed distance from Well bottom |  |  | 0.1 | m
Pump Station Top of Slab (TOS) |  |  | 3.5 | m RL
Overflow Level |  |  | 2.15 | m RL
Emergency Storge (if not present = Invert?) |  |  | 2 | m RL
Invert Level |  |  | -0.85 | m RL
TWL (Duty Pump Start) |  |  | -2.24 | m RL
BWL (Duty Pump Stop) |  |  | -2.7 | m RL
Well Bottom |  |  | -3.15 | m RL
Wet Well Diameter (Mtrs) |  |  | 1.5 | m
One Pump Flow Rate |  |  | 17 | L/s
Both Pump(s) Flow Rate |  |  | 20 | L/s
Notes:
1) Values shall be taken from "As Built" drawings where available
Calculated Install Dimensions
|  |  | Value | Unit
Total Well Depth |  |  | 6.65 | m TOS
Hydrostatic Install location |  |  | 6.55 | m TOS
Overflow Probe |  |  | 1.35 | m TOS
Emergency Start Float |  |  | 1.85 | m TOS
Emergency Storage Invert |  |  | 1.5 | m TOS
Top Water level (Invert) |  |  | 5.74 | m TOS
Duty Pumping Distance |  |  | 0.46 | m TOS
Duty Pump-down Time = 1 Pump |  |  | 191.2676 | seconds
Well Pump-down Time = 2 Pumps |  |  | 162.5774 | seconds
Note:
1) Pump-down times assume no inflow
2) The Top of Slab (TOS) dimensions are measured from top of slab level
Actual Setup Levels
|  |  | Value | Unit | HMI
Overflow |  |  | 1.35 | m TOS | 100%
Emergency Sorage Invert |  |  | 1.5 | m TOS | 90%
Asisist Start Point |  |  | 5.7 | m TOS | 20%
Duty Start Point |  |  | 5.8 | m TOS | 15%
Assist Stop Point |  |  | 5.95 | m TOS | 10%
Duty Stop Point |  |  | 6 | m TOS | 7%
Control Setup |  |  | 0-100 | %
Rising Main Volume
Rising Main Volume Calculation
Measurement | Length | Internal Diam | Volume
Units | (m) | (mm) | (kL)
| 1 | 1000 | 0.7854
| Hydrostatic (Well Level) Calculations |  |  |  |  | Installations
| Calculated Well Probe (Sensor to TOS) |  |  | 6.55 | Metres
| Calc Well Probe (Sensor to 100% - Overflow) |  |  | 5.2 |  | Installed Probe Length | 6.4313 | Metres
| Calc Well Probe (Sensor to Overflow 120%) |  |  | 6.24
[6 empty] | Installed 0-100% Span | 5.0813 | Metres
| Calculated Probe Length |  |  | 6.4313 | Metres | Installed 0-100% Span | 12.13 | mAmps
| Calculated 0-100% Span |  |  | 5.0813 | Metres
| Calculated 0-100% Span |  |  | 12.13 | mAmps | Calculated 0 Off-Set | 0 | %
| Calculated Control Span |  |  | 2.3125 | Metres
[7 empty] | Scada |  | Multitrode
| Calculated Control Span |  |  | 45.5105 | % |  | % |  | %
| Control 100 % Level |  |  | -0.61875 | Mtrs RL | Control 100 % Level 100 | 45.5105 |  | 45.5
| Control High Alarm ON |  |  | -0.85 | Mtrs RL | Control High Alarm ON 80 | 40.9594 |  | 41
| Control High Alarm OFF |  |  | -1.0813 | Mtrs RL | Control High Alarm OFF 70 | 36.4084 |  | 36.5
| Standby Pump Start |  |  | -1.3125 | Mtrs RL | Standby Pump Start 70 | 31.8573 |  | 32
| Duty Pump Start |  |  | -1.5438 | Mtrs RL | Duty Pump Start 60 | 27.3063 |  | 27.5
| Standby Pump Stop |  |  | -2.4688 | Mtrs RL | Standby Pump Stop 20 | 9.1021 |  | 9
| Duty Pump Stop |  |  | -2.7 | Mtrs RL | Duty Pump Stop 10 | 4.551 |  | 4.5
| Control Zero |  |  | -2.9313 | Mtrs RL | Control Zero 0 | 0 |  | 0
Insert Wet Wet Dimension Diagram.
Include all RL levels and any additional useful information for easy value verification (As-Built).
EXAMPLE

## Drawdown
| Project Name: |  |  | Name | [7 empty] | Project Name: | Name
| Finance No: |  |  | No | [7 empty] | Finance No: | No
| Project Address: |  |  | Address | [7 empty] | Project Address: | Address
Drawdown Test
Well Volume
Measurement | Diameter | Depth | Volume
Units | (m) | (m) | (m³)
| 1.5 | 6.65 | 11.7515
Flowmeter Verification
| Before Running |  | Running | After Running |  |  | Calculated Results
Measurement | Start Level | Start Level | Flow | Finish Level | Finish Level | Running Time | Drawdown | Flowrate
Device | HMI | TOS | Flowmeter | HMI | TOS | Timer
Units | (%) | (mm) | (L/s) | (%) | (mm) | (seconds) | (mm) | (L/s)
Pump1 | 0 | 0 | 0 | 0 | 0 | 0 | No Values | No Values
Pump2 | 0 | 0 | 0 | 0 | 0 | 0 | No Values | No Values
Pump 1 and 2 | 0 | 0 | 0 | 0 | 0 | 0 | No Values | No Values
Level Sensor Checks |  |  |  |  | High Level Alarm |  |  |  | High High Level Alarm
Measurement | Level | Level | Level |  | Level | Level | Level |  | Level | Level | Level
Device | HMI | TOS | TOS |  | HMI | TOS | TOS |  | HMI | TOS | TOS
Units | (%) | (mm) | (mm) |  | (%) | (mm) | (mm) |  | (%) | (mm) | (mm)
| 100% | 1.35 | 0 |  | 90.38% | 1.85 | 0 |  | 100% | 1.35 | 0
| 75% | 2.65 | 0
| 50% | 3.95 | 0
| 25% | 5.25 | 0
| 0% | 6.55 | 0
Pump Test
Pump Performance
Tender Pump Curve
Measurement | Head | Flow (1P) | Flow (2P)
Units | (m) | (L/s) | (L/s)
| 10 | 0 | 0
| 9 | 200 | 400
| 7 | 400 | 800
| 4 | 600 | 1200
| 0 | 800 | 1600
As Constructed Pump Curve
Pump 1
Measurement | Water Level | Guage Level | Head | Head | Motor Amps | Flow
Device | TOS | TOS | Guage |  | Drive | Flowmeter
Units | (mm) | (mm) | (KPa) | (m) | (A) | (L/s)
Discharge Valve(s) Closed | 0 | 0 | 100 | 10.1937 | 0 | 0
Discharge Valve(s) Pos 1 | 0 | 0 | 90 | 9.1743 | 0 | 200
Discharge Valve(s) Pos 2 | 0 | 0 | 70 | 7.1356 | 0 | 400
Discharge Valve(s) Pos 3 | 0 | 0 | 40 | 4.0775 | 0 | 600
Discharge Valve(s) Open | 0 | 0 | 0 | 0 | 0 | 800
Pump 2
Measurement | Water Level | Guage Level | Head | Head | Motor Amps | Flow
Device | TOS | TOS | Guage |  | Drive | Flowmeter
Units | (mm) | (mm) | (KPa) | (m) | (A) | (L/s)
Discharge Valve(s) Closed | 0 | 0 | 100 | 10.1937 | 0 | 0
Discharge Valve(s) Pos 1 | 0 | 0 | 90 | 9.1743 | 0 | 200
Discharge Valve(s) Pos 2 | 0 | 0 | 70 | 7.1356 | 0 | 400
Discharge Valve(s) Pos 3 | 0 | 0 | 40 | 4.0775 | 0 | 600
Discharge Valve(s) Open | 0 | 0 | 0 | 0 | 0 | 800
Pumps 1 and 2 (Parallel)
Measurement | Water Level | Guage Level | Head | Head | Motor Amps | Flow
Device | TOS | TOS | Guage |  | Drive | Flowmeter
Units | (mm) | (mm) | (KPa) | (m) | (A) | (L/s)
Discharge Valve(s) Closed | 0 | 0 | 100 | 10.1937 | 0 | 0
Discharge Valve(s) Pos 1 | 0 | 0 | 90 | 9.1743 | 0 | 400
Discharge Valve(s) Pos 2 | 0 | 0 | 70 | 7.1356 | 0 | 800
Discharge Valve(s) Pos 3 | 0 | 0 | 40 | 4.0775 | 0 | 1200
Discharge Valve(s) Open | 0 | 0 | 0 | 0 | 0 | 1600
Insert Design Pump Curve.
Provide detailed pump information.
EXAMPLE
EXAMPLE

## SS, VFD, DOL Settings
| Project Name: | Name
| Finance No: | No
| Project Address: | Address
Soft Starter Settings
Variable Flow Drive Settings
Direct On-line Overload Settings

## Flowmeter Settings
| Project Name: |  | Name
| Finance No: |  | No
| Project Address: |  | Address
Flowmeter Settings (WaterMaster)
Parameters | Defaults | Actual Settings |  | Parameters | Defaults | Actual Settings
Easy Setup |  |  |  | Device Setup
Language | English |  |  | Access
Flowrate Unit | Q (flowrate) Unit l/s |  |  | Standard Password
Qmax | 900Lt/s |  |  | Advanced Password
Volume & Pulse Unit | M3 |  |  | Client Enable | HMI/HART
Pulse Width | 450ms |  |  | Read Only Switch | Inactive
Pulses / Unit | 1 |  |  | Operating Mode
Damping | 3s |  |  | Meter Mode | Forward & Reverse
Mains Frequency | 50Hz |  |  | Flow Indication | Normal
Units
Device Info |  |  |  | Volume & Pulse Unit | 1
Manufacturer |  |  |  | Q (Flowrate) Unit | l/s
Name | ABB Limited |  |  | Velocity Unit | m/s
Address 1 | Stonehouse UK |  |  | Qmax DN
Address 2 | GL10 3TA |  |  | Qmax DN | 1750 l/s
Contact | 44 (0) 1453 826661 |  |  | Qmax | 500 l/s
Sensor |  |  |  | Damping | 3.00 s
Type | WM Full Bore |  |  | User Span | 1
Size | DN500 |  |  | Mains Frequency | 50 Hz
Qmax DN | 1750 l/s |  |  | Calibration Factors
TAG & ID |  |  |  | Low Flow Cutoff
Location Tag | ? |  |  | Low Flow Cutoff Level | 0
Sensor Tag | ? |  |  | hysterisis | 0.2
Sensor ID | 2511 |  |  | User Zero
SAP / ERP No. | 3K220000026602 |  |  | Manual Adjust | 0.00 mm/s
Term Board S/W | 01.0300/000 01052007 |  |  | Auto Adjust | Blank
First cal date | 03:41:47 ---- 2009-10-15 |  |  | Calibration Factors
Last cal date | 03:41:50 ---- 2009-10-15 |  |  | Span Ss | 1.455
Cal. Cert No | ---- 09/1/9/214425 |  |  | Zero Sz | 0.04 mm/s
Last Cal Location | Stonehouse |  |  | Trim St | 0
Cal Mode | WaterMaster |  |  | Calibration Mode | WaterMaster
Properties |  |  |  | Sensor Cal | OIML Class 1
Electrode Material | Stainless Steel |  |  | Drive Mode | 5A
Lining Material | Elastomer |  |  | Excitation Current | 180mA
Sensor Run Hrs | 556hrs 50mins |  |  | Factory Cutoff | 5.0 mm/s
Transmitter |  |  |  | Fact.Cutoff No.Av. | 4
Tx Type |  |  |  | Cal Status | Calibrated
Tx Type | Watermaster |  |  | Sv | 0.00 m2/s
Tx Run Hrs | 557hrs 55mins |  |  | Sc | 0%
Tag & Id |  |  |  | Coil Measurement F | 20.0 Hz
Tx Tag | FET-WRT-AC
Tx Id | 5603 |  |  | Display
Tx Pin | 2 |  |  | Language
SAP / ERP No. | 3K220000040401 |  |  | Language | English
Tx Version |  |  |  | Flowrate Format | x.xx
Application | V01.02.00 - 13/11/09 |  |  | Volume Format | x
Application CRC | 0x5849 |  |  | Date / Time Format | YYYY/MM/DD
Hart F/W | 00.00.04 |  |  | Contrast | 50
Boot Loader | 01.00.05 - 05/11/2009 |  |  | Operator Pages
H/W | 01.00.02 |  |  | Operator Pages 1
Tx Calibration |  |  |  | Display Mode | 1 x 6
First cal date | 01:55:47 ---- 2010-01-29 |  |  | 1st Line | Volume Flowrate
Last cal date | 01:55:47 ---- 2010-01-29
Operator Pages 2
|  |  |  | Display Mode | 3 x 9
|  |  |  | 1st Line | Volume Flowrate
|  |  |  | 2nd Line | Volume Forward
|  |  |  | 3rd Line | Volume Reverse
Operator Pages 3
Flowrate Format
Volume Format
Display Test
Language

## Notes
This worksheet has is designed for sewer pumping stations with 2 identical pumps in a duty standby configuration.
For pump stations with more than 2 pumps, the worksheet shall be modified accordingly.